## Sheet1
Cooling Load Calculation For Conference Hall 01:-
Design Conditions:- |  |  | Given Data:-
Location | Guwahati |  | Room Entering air Temp.
Outdoor DBT | 35°C |  | Coil Temp. | 7°C | h(inside air)(Btu/h-ft^2-F) | 3.522
Outdoor RH | 90% |  | Recirculation | 70% | h(outside air)(Btu/h-ft^2-F) | 8.805
Indoor DBT | 25°C |  | Max/Min temperature | 35°C/25°C | h(air-cocerete)(Btu/h-ft^2-F) | 0.8805
Indoor RH | 50% |  | Range | 10°C | h(air-wood)(Btu/h-ft^2-F) | 1.76
Wind Velocity | 3.1 Kmph |  | Maximum outdoor | 35°C | k(brick)(Btu/h-ft-F) | 0.462
Month under consideration | July |  | Mean outdoor temperature | 32°C | k(concerete)(Btu/h-ft-F) | 0.167
[5 empty] | k(roof tiles)(Btu/h-ft-F) | 0.48
Calculation for Lecture hall 1:-
Specifications(In SI Units):- |  |  | Quantity |  | Total Rated Power(W)
Lights |  |  | 42(each 100W)
Speakers |  |  | 04(each 150W) | 13 inch | 600
Projector and UPS |  |  | 02(each 500W) | (3000-4000 lumen) | 1000
No of Persons |  |  | 130 | 17-40 years age group
Calculations for Structures:-
WALLS
Type | Length (ft) | Height (ft) | Area (ft^2) | Door/Window | Remaining area | CLTD/TD | Inside design Temp (TR) | Mean outdoor Temp (TM) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
NORTH | 56.5 | 17 | 960.5 | 0 | 960.5 | 10 | 77 | 89.6 | 10 | 0.1452 | 1394.646
WEST | 34.5 | 17 | 586.5 | 2 Doors | 514.5 | 10 | 77 | 89.6 | 10 | 0.1452 | 747.054
SOUTH | 56.5 | 17 | 960.5 | 0 | 960.5 | 10 | 77 | 89.6 | 10 | 0.1452 | 1394.646
EAST | 34.5 | 17 | 586.5 | 1 Door | 550.5 | 34 | 77 | 89.6 | 36 | 0.1489 | 2950.9002
[10 empty] | Total | 6487.2462
ROOFS
Type | Length (ft) | Area (ft^2) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
Concrete roof on which clay tiles are placed with false ceiling and sound absorbing material | 56.5 | 1949.25 | 25 | 0.1504 | 7329.18
FLOOR
Type | Length (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load
Concrete flooring with tiles | 56.5 | 1949.25 | 27 | 0.258 | 13578.4755
DOORS
Type | Length (ft) | Width (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load | 3 Doors
Wooden Door | 8 | 4.5 | 36 | 10 | 0.288 | 103.68 | 311.04
Calculations for People:-
Type | Persons | SHG/LHG | CLF | Cooling load
Sensible | 130 | 220 | 0.77 | 22022
Latent | 130 | 280 | 1 | 36400
Calculations for Lights:-
Type | Conversion factor | Rated Power | CLF | Ballast Factor | Number of lights | Cooling load
100 W LED bulbs | 3.4 | 100 | 0.45 | 1.3 | 42 | 8353.8
Calculations for Appliances:-
Type |  | Conversion factor | Rated Power | CLF | Usage factor | Radiation factor | Quantity | Cooling load
Speakers | Sensible Load | 3.4 | 150 | 1 | 1 | 0.15 | 4 | 306
| Latent Load | 3.4 | 150 |  | 1 |  | 4 | 2040
Projector and UPS | Sensible Load | 3.4 | 500 | 0.4 | 0.3 | 0.2 | 2 | 81.6
| Latent Load | 3.4 | 500 |  | 0.3 |  | 2 | 1020
[6 empty] | Total | 10 | 3447.6
Calculations for Ventilation:-
Type | Constant | CFM | TD( To-Tc) | Number of persons | Cooling load
Sensible | 1.08 | 5.5 | 25 | 130 | 19305
Type | Constant | CFM | HD( Wo-Wc) | Number of persons | Cooling load
Latent | 4840 | 5.5 | 0.0245 | 130 | 84784.7
Calculations for Infiltration:-
Type | Constant | CFM | TD( To-Ti) | Number of persons | Cooling load
Sensible | 1.08 | 5.5 | 10 | 130 | 7722
Type | Constant | CFM | HD( Wo-Wi) | Number of persons | Cooling load
Latent | 4840 | 5.5 | 0.0225 | 130 | 77863.5
Summary
Cooling Load Components | Sensible load | Latent load | TOTAL LOAD IN Btu/hr
WALLS | 6487.2462 | 0 | 6487.2462
ROOFS | 7329.18 | 0 | 7329.18
DOORS | 311.04 | 0 | 311.04
LIGHTS | 8353.8 | 0 | 8353.8
PEOPLE | 22022 | 36400 | 58422
APPLIANCES | 387.6 | 3060 | 3447.6
INFILTRATION | 7722 | 77863.5 | 85585.5
VENTILATION | 19305 | 84784.7 | 104089.7
Total | 71917.8662 | 202108.2 | 274026.0662 | TONNES OF REFERIGERATION
Room Total sensible Load | 44890.8662 |  |  | 22.8355
Room Total latent Load |  | 39460
Total room load |  |  | 84350.8662
Sensible heat factor | 0.53219

## Sheet2
Cooling Load Calculation For Conference Hall 02:-
Design Conditions:- |  |  | Given Data:-
Location | Guwahati |  | Room Entering air Temp.
Outdoor DBT | 35°C |  | Coil Temp. | 7°C | h(inside air)(Btu/h-ft^2-F) | 3.522
Outdoor RH | 90% |  | Recirculation | 70% | h(outside air)(Btu/h-ft^2-F) | 8.805
Indoor DBT | 25°C |  | Max/Min temperature | 35°C/25°C | h(air-cocerete)(Btu/h-ft^2-F) | 0.8805
Indoor RH | 50% |  | Range | 10°C | h(air-wood)(Btu/h-ft^2-F) | 1.76
Wind Velocity | 3.1 Kmph |  | Maximum outdoor | 35°C | k(brick)(Btu/h-ft-F) | 0.462
Month under consideration | July |  | Mean outdoor temperature | 32°C | k(concerete)(Btu/h-ft-F) | 0.167
[5 empty] | k(roof tiles)(Btu/h-ft-F) | 0.48
Calculation for Lecture hall 1:-
Specifications(In SI Units):- |  |  | Quantity |  | Total Rated Power(W)
Lights |  |  | 54(each 100W)
Speakers |  |  | 04(each 150W) | 13 inch | 600
Projector and UPS |  |  | 02(each 500W) | (3000-4000 lumen) | 1000
No of Persons |  |  | 130 | 17-40 years age group
Calculations for Structures:-
WALLS
Type | Length (ft) | Height (ft) | Area (ft^2) | Door/Window | Remaining area | CLTD/TD | Inside design Temp (TR) | Mean outdoor Temp (TM) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
NORTH | 56.5 | 17 | 960.5 | 0 | 960.5 | 10 | 77 | 89.6 | 10 | 0.1452 | 1394.646
WEST | 44.75 | 17 | 760.75 | 2 Doors | 688.75 | 10 | 77 | 89.6 | 10 | 0.1452 | 1000.065
SOUTH | 56.5 | 17 | 960.5 | 0 | 960.5 | 10 | 77 | 89.6 | 10 | 0.1452 | 1394.646
EAST | 44.75 | 17 | 760.75 | 1 Door | 724.75 | 34 | 77 | 89.6 | 36 | 0.1489 | 3884.9499
[10 empty] | Total | 7674.3069
ROOFS
Type | Length (ft) | Area (ft^2) | Corrected CLTD | Overall heat transfer coefficient | Cooling load
Concrete roof on which clay tiles are placed with false ceiling and sound absorbing material | 56.5 | 2528.375 | 25 | 0.1504 | 9506.69
FLOOR
Type | Length (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load
Concrete flooring with tiles | 56.5 | 2528.375 | 27 | 0.258 | 17612.6603
DOORS
Type | Length (ft) | Width (ft) | Area (ft^2) | TD | Overall heat transfer coefficient | Cooling load | 3 Doors
Wooden Door | 8 | 4.5 | 36 | 10 | 0.288 | 103.68 | 311.04
Calculations for People:-
Type | Persons | SHG/LHG | CLF | Cooling load
Sensible | 200 | 220 | 0.77 | 33880
Latent | 200 | 280 | 1 | 56000
Calculations for Lights:-
Type | Conversion factor | Rated Power | CLF | Ballast Factor | Number of lights | Cooling load
100 W LED bulbs | 3.4 | 100 | 0.45 | 1.3 | 54 | 10740.6
Calculations for Appliances:-
Sensible
Type |  | Conversion factor | Rated Power | CLF | Usage factor | Radiation factor | Quantity | Cooling load
Speakers | Sensible Load | 3.4 | 150 | 1 | 1 | 0.15 | 4 | 306
| Latent Load | 3.4 | 150 |  | 1 |  | 4 | 2040
Projector and UPS | Sensible Load | 3.4 | 500 | 0.4 | 0.3 | 0.2 | 2 | 81.6
| Latent Load | 3.4 | 500 |  | 0.3 |  | 2 | 1020
[6 empty] | Total | 10 | 3447.6
Calculations for Ventilation:-
Type | Constant | CFM | TD( To-Tc) | Number of persons | Cooling load
Sensible | 1.08 | 5.5 | 25 | 200 | 29700
Type | Constant | CFM | HD( Wo-Wc) | Number of persons | Cooling load
Latent | 4840 | 5.5 | 0.0245 | 200 | 130438
Calculations for Infiltration:-
Type | Constant | CFM | TD( To-Ti) | Number of persons | Cooling load
Sensible | 1.08 | 5.5 | 10 | 200 | 11880
Type | Constant | CFM | HD( Wo-Wi) | Number of persons | Cooling load
Latent | 4840 | 5.5 | 0.0225 | 200 | 119790
Summary
Cooling Load Components | Sensible load | Latent load | TOTAL LOAD IN Btu/hr
WALLS | 7674.3069 | 0 | 7674.3069
ROOFS | 9506.69 | 0 | 9506.69
DOORS | 311.04 | 0 | 311.04
LIGHTS | 10740.6 | 0 | 10740.6
PEOPLE | 33880 | 56000 | 89880
APPLIANCES | 387.6 | 3060 | 3447.6
INFILTRATION | 11880 | 119790 | 131670
VENTILATION | 29700 | 130438 | 160138
Total | 104080.2369 | 309288 | 413368.2369 | TONNES OF REFERIGERATION
Room Total sensible Load | 62500.2369 |  |  | 34.4474
Room Total latent Load |  | 59060
Total room load |  |  | 121560.2369
Sensible heat factor | 0.51415