## Slide 1
COLLING LOAD CALCULATION OF CONFERENCE HALL 1 & 2 OF MECHANICAL DEPARTMENT, IIT GUWAHATI
Presented by
Nikhil Kumar (214103315)
Rishabh Sharma (214103333)

## Slide 2
Orientation of building
Physical dimensions of spaces
Ceiling height
Construction materials
Windows
Doors
People (occupancy- nature of activity)
Lighting
Appliances
Ventilation and infiltration
Key information for load estimation

## Slide 3
Specification of Conference Hall
Parameter | Conference Hall 1 | Conference Hall 2
Length (ft) | 56.5 | 56.5
Width (ft) | 34.5 | 44.75
Height (ft) | 17 | 17
Thickness of wall (ft) | 1.75 | 1.75
Number of door | 3 | 3
Height of door (ft) | 2.33 | 2.33
Thickness of door (ft) | 3 | 3
Width of door (ft) | 4.5 | 4.5
Number of people | 130 | 200
Total lights | 42 | 54
Number of speakers | 4 | 4
Number of projectors | 2 | 2

## Slide 4
DESIGN CONSIDERATIONS
Outdoor Design Condition:
at peak time, DBT= 95˚F(35˚C),
90% RH (for Guwahati)
Indoor Design Condition:
at peak time, DBT= 77˚F(25˚C),
50% RH

## Slide 7
CALCULATION OF CLTD CORRECTION
 | CLTD (˚F) | CLTDc (˚F)
East wall | 34 | 36
CONFERENCE HALL 1
CONFERENCE HALL 2
CLTDC = [CLTD + (78 – TR) +(TM – 85)]
Where
TR= inside design temp= 77˚ F
Daily range= max DBT- min DBT
= 35-25 = 10˚ C (from Guwahati climate graph)
TM=Mean outdoor temp= Max outdoor temperature-(Daily range/2)
= 35-10/2= 30˚ C or 86˚ F
 | CLTD (˚F) | CLTDc (˚F)
East wall | 34 | 36

## Slide 8: Calculation of overall Heat transfer co-coefficient
For roof
Btu/hr.ft².°F

## Slide 9: Calculation of overall Heat transfer co-coefficient
For interior walls
Btu/hr.ft².°F

## Slide 10: Calculation of overall Heat transfer co-coefficient
For exterior walls
Btu/hr.ft².°F

## Slide 11: Calculation of heat load through wall
EXTERIOR WALL
Q= U×A× CLTDc
 | Area | CLTDc (˚F) | U | Q (btu/hr)
East wall | 550.5 | 36 | 0.1489 | 2950.9
CONFERENCE HALL 1
CONFERENCE HALL 2
 | Area | CLTDc (˚F) | U | Q (btu/hr)
East wall | 724.75 | 36 | 0.1489 | 3884.94

## Slide 12: Calculation of heat load through wall
 | A | ∆T | U | Q (btu/hr)
North wall | 960.5 | 10 | 0.1452 | 1394.64
South wall | 960.5 | 10 | 0.1452 | 1394.64
West wall | 514.5 | 10 | 0.1452 | 747.05
Q=U*A*∆T
CONFERENCE HALL 1
CONFERENCE HALL 2
 | A | ∆T | U | Q (btu/hr)
South wall | 960.5 | 10 | 0.1452 | 1394.64
North wall | 960.5 | 10 | 0.1452 | 1394.64
West wall | 688.75 | 10 | 0.1452 | 1000
INTERIOR WALL

## Slide 13: Calculation of heat load through Roof
 | Area | CLTDc (˚F) | U | Q (btu/hr)
Conference hall 1 | 1949.25 | 25 | 0.1504 | 7329.18
Conference hall 2 | 2528.375 | 25 | 0.1504 | 9506.69
For Roof
Q= U×A× CLTDc

## Slide 14: Calculation of people load
CONFERENCE HALL 1
Assumption: Standing, walking slowly
SGH= 220 Btu/hr ,LGH=280 Btu/hr
N=130
Qs =130×220×0.77 = 22022 Btu/hr
Ql = 130×280 = 36400 Btu/hr
Q s (Btu/hr) = N (number of people) x SHG (Btu/hr) x CLF
Q l (Btu/hr) = N (number of people) x LHG (Btu/hr
Assumption: (10 hrs per day work )
CLF=0.77
For People load calculation
CONFERENCE HALL 1
Assumption: Standing, walking slowly
SGH= 220 Btu/hr ,LGH=280 Btu/hr
N=200
Qs =200×220×0.77 = 33880 Btu/hr
Ql = 200×280 = 56000 Btu/hr

## Slide 15: Calculation of lighting load
For Light load calculation
CLF = 0.45
(Assumption : Heavy weight, Simple Furnishings, no carpet and V* < 0.5, Where V * is the air supply rate in CFM per sq. foot of floor area)
 | Conversion factor | Number of lights | CLF | F(B) | W(rated power) | Q (btu/hr)
Conference hall 1 | 3.4 | 42 | 0.45 | 1.3 | 100 | 8353.5
Conference hall 2 | 3.4 | 54 | 0.45 | 1.3 | 100 | 10740.6
Q (Btu/hr) = 3.4[Btu/hr /Watt] * CLF * W * f(b)

## Slide 16: Calculation of window-Door load
 | Td | A | N | U | Q (btu/hr)
Conference hall 1 | 10 | 36 | 3 | 0.288 | 311.04
Conference hall 2 | 10 | 36 | 3 | 0.288 | 311.04
Window:
There will be no load for window in conference hall 1 and 2
Door:

## Slide 17
Calculation of load though appliances
CONFERENCE HALL 1
 | W | Fu | Fr | NUMBER(N) | CLF | Qsensible | Qlatent
Projector | 500 | 0.3 | 0.2 | 2 | 0.45 | 91.8 | 1020
Speaker | 150 | 1 | 0.15 | 4 | 0.45 | 137.7 | 2040
CONFERENCE HALL 2
Q Sensible = Qin x Fu x Fr x (CLF)
Q Latent = Qin x Fu
Qin = 3.4 x W, CLF = 0.45 (simple furnishing)
Fu= Usage factor ,Fr= Radiation factor ,CLF = Cooling Load Factor
 | W | Fu | Fr | NUMBER(N) | CLF | Qsensible | Qlatent
Projector | 500 | 0.3 | 0.2 | 2 | 0.45 | 91.8 | 1020
Speaker | 150 | 1 | 0.15 | 4 | 0.45 | 137.7 | 2040

## Slide 18
Calculation of infiltration load
1. Sensible Heat | CFM | ΔT | No of people | Q (btu/hr)
Educational Institute | 5.5 | 10 | 130 | 7722
2. Latent Heat | CFM | ΔW | No of people | Q
 | 5.5 | 0.022 | 130 | 77863.5
Q Sensible= 1.08 * CFM * ΔT
Q Latent= 4840 * CFM * ΔW
Assumption: Educational institute
CFM(cubic feet of air per minute)=5.5
CONFERENCE HALL 1
CONFERENCE HALL 2
1. Sensible Heat | CFM | ΔT | No of people | Q (btu/hr)
Educational Institute | 5.5 | 10 | 200 | 11880
2. Latent Heat | CFM | ΔW | No of people | Q
 | 5.5 | 0.022 | 200 | 119790

## Slide 19
Calculation of room total load
CONFERENCE HALL 1
SECTION | SHL(BTU/hr) | LHL(BTU/hr) | Total(BTU/hr)
WALLS | 6487.2463 |  | 6487.2463
Roof | 7329.18 |  | 7329.18
Light | 8353.8 |  | 8353.8
DOORS | 311.04 |  | 311.04
Electrical Appliances | 229.5 | 3060 | 3289.5
People | 22022 | 36400 | 58422
infiltration | 7722 | 77863.5 | 85585.5
Total |  |  | 159936.366
Total(TR) |  |  | 14.16

## Slide 20
CONFERENCE HALL 2
SECTION | SHL(BTU/hr) | LHL(BTU/hr) | Total(BTU/hr)
WALLS | 7674,3069 |  | 7674.3069
Roof | 9506.69 |  | 9506.69
Light | 10740.6 |  | 10740.6
DOORS | 311.04 |  | 311.04
Electrical Appliances | 387.6 | 3060 | 3289.5
People | 33880 | 56000 | 89880
infiltration | 11880 | 119790 | 131670
Total |  |  | 253230.2369
Total(TR) |  |  | 21.10

## Slide 21
1. Sensible Heat | CFM | ΔT | No of persons | Q (btu/hr)
Educational Institute | 5.5 | 25 | 130 | 19305
2. Latent Heat | CFM | ΔW | No of persons | Q (btu/hr)
 | 5.5 | 0.0245 | 130 | 84784.7
Calculation of ventilation load
Q Sensible= 1.08 * CFM * ΔT
Q Latent= 4840 * CFM * ΔW
1. Sensible Heat | CFM | ΔT | No of persons | Q (btu/hr)
Educational Institute | 5.5 | 25 | 200 | 29700
2. Latent Heat | CFM | ΔW | No of persons | Q (btu/hr)
 | 5.5 | 0.0245 | 200 | 130438
CONFERENCE HALL 1
CONFERENCE HALL 2

## Slide 22
Calculation of Total load with ventilation
CONFERENCE HALL 1
SECTION | SHL(BTU/hr) | LHL(BTU/hr) | Total(BTU/hr)
WALLS | 6487.2463 |  | 6487.2463
Roof | 7329.18 |  | 7329.18
Light | 8353.8 |  | 8353.8
DOORS | 311.04 |  | 311.04
Electrical Appliances | 229.5 | 3060 | 3289.5
People | 22022 | 36400 | 58422
infiltration | 7722 | 77863.5 | 85585.5
Ventilation | 19305 | 84784.7 | 104089.7
Total |  |  | 274026.06
Total(TR) |  |  | 22.835

## Slide 23
Chart: 
| WALLS | ROOFS | DOORS | LIGHTS | PEOPLE | APPLIANCES | INFILTRATION | VENTILATION | Total | Room Total sensible Load | Room Total latent Load
cooling load component | 6487.2462 | 7329.18 | 311.04 | 8353.8 | 58422 | 3447.6 | 85585.5 | 104089.7

## Slide 24
Calculation of total load
CONFERENCE HALL 2
SECTION | SHL(BTU/hr) | LHL(BTU/hr) | Total(BTU/hr)
WALLS | 7674,3069 |  | 7674.3069
Roof | 9506.69 |  | 9506.69
Light | 10740.6 |  | 10740.6
DOORS | 311.04 |  | 311.04
Electrical Appliances | 387.6 | 3060 | 3289.5
People | 33880 | 56000 | 89880
infiltration | 11880 | 119790 | 131670
Ventilation | 29700 | 130438 | 160138
Total |  |  | 413368.236
Total(TR) |  |  | 34.447

## Slide 25
Chart: 
| WALLS | ROOFS | FLOOR | DOORS | LIGHTS | PEOPLE | APPLIANCES | INFILTRATION | VENTILATION
cooling load distribution | 15357.9737 | 7329.18 | 6034.878 | 99.36 | 23868 | 44310 | 387.6 | 131670 | 171155.6

## Slide 26
Sensible heat factor | Bypass factor | Cooling coil efficiency (%)
0.532 | 0.15 | 85
For hall 1
To = 35 °C
Ti = 25 °C
Tc = 10 °C
Assumption : 20% fresh air for ventilation
Air entering to room = 21 °C
SHF = room sensible load / total room load
BPF =
Cooling coil efficiency = 1-BPF

## Slide 27
a
e
d
c
b

## Slide 28
Sensible heat factor | Bypass factor | Cooling coil efficiency (%)
0.514 | 0.15 | 85
For hall 2
To = 35 °C
Ti = 25 °C
Tc = 10 °C
Assumption : 20% fresh air for ventilation
Air entering to room = 21 °C
SHF = room sensible load / total room load
BPF =
Cooling coil efficiency = 1-BPF

## Slide 29
a
e
d
c
b

## Slide 30: References
ASHRAE Handbook, 2001
COOLING LOAD PPT Course ME621

## Slide 31
Thank you